Solar Energy:

Introduction:

Solar energy is an important, clean, cheap and abundantly available renewable energy. It is received on Earth in cyclic, intermittent and dilute form with very low power density 0 to 1 kW/m2.Solar energy received on the ground level is affected by atmospheric clarity, degree of latitude, etc. For design purpose, the variation of available solar power, the optimum tilt angle of solar flat plate collectors, the location and orientation of the heliostats should be calculated.

Units of solar power and solar energy:

In SI units, energy is expressed in Joule. Other units are angley and Calorie where

1 angley = 1 Cal/cm2.day

1 Cal = 4.186 J

For solar energy calculations, the energy is measured as an hourly or monthly or yearly average and is expressed in terms of kJ/m2/day or kJ/m2/hour. Solar power is expressed in terms of W/m2 or kW/m2.

Essential subsystems in a solar energy plant:

- Solar collector or concentrator: It receives solar rays and collects the energy. It may be of following types:

- Flat plate type without focusing

- Parabolic trough type with line focusing

- Paraboloid dish with central focusing

- Fresnel lens with centre focusing

- Heliostats with centre receiver focusing

- Energy transport medium: Substances such as water/ steam, liquid metal or gas are used to

transport the thermal energy from the collector to the heat exchanger or thermal storage. In solar PV systems energy transport occurs in electrical form.

- Energy storage: Solar energy is not available continuously. So we need an energy storage medium for maintaining power supply during nights or cloudy periods. There are three major types of energy

storage: a) Thermal energy storage; b) Battery storage; c) Pumped storage hydro-electric plant.

- Energy conversion plant: Thermal energy collected by solar collectors is used for producing steam, hot water, etc. Solar energy converted to thermal energy is fed to steam-thermal or gas-thermal power plant.

Department of Electrical Engineering, Veer Surendra Sai University of Technology Burla	Page 30

- Power conditioning, control and protection system: Load requirements of electrical energy vary with time. The energy supply has certain specifications like voltage, current, frequency, power etc.

The power conditioning unit performs several functions such as control, regulation, conditioning,

protection, automation, etc.

Fig Subsystems in solar thermal energy conversion plants

- Alternative or standby power supply: The backup may be obtained as power from electrical

network or standby diesel generator.

Energy from the sun:

The sun radiates about 3.8 x 1026 W of power in all the directions. Out of this about 1.7 x 1017 W is     received by earth. The average solar radiation outside the earth’s atmosphere is 1.35 kW/m2 varying from 1.43 kW/m2 (in January) to 1.33 kW/m2(in July).

Solar thermal energy (STE) is a form of energy and a technology for

harnessing solar energy to generate thermal energy or electrical energy for use in industry,

and in the residential and commercial sectors. The first installation of solar thermal energy equipment occurred in the Sahara Desert approximately in 1910

when a steam engine was run on steam produced by sunlight. Because liquid fuel engines were developed and found more convenient, the Sahara project was abandoned, only to be revisited several decades late.

Solar thermal collectors are classified by the United States Energy Information Administration as low-, medium-, or high-temperature collectors. Low-temperature collectors are flat plates generally used to heat swimming pools. Medium-temperature collectors are also usually flat plates but are used for heating water or air for residential and commercial use. High-temperature collectors concentrate sunlight using mirrors or lenses and are generally used for fulfilling heat requirements up to 300 deg C / 20 bar pressure in industries, and for electric power production. However, there is a term that used for both the applications. Concentrated Solar Thermal (CST) for fulfilling heat requirements in industries and Concentrated Solar Power (CSP) when the heat collected is used for power generation. CST and CSP are not replaceable in terms of application.

The 377 MW Ivanpah Solar Power Facility is the largest solar power plant in the world, located in the Mojave Desert of California. Other large solar thermal plants include the SEGS installation (354 MW), also in the Mojave, as well as the Solnova Solar Power Station (150 MW), the Andasol solar power station (150 MW), and Extresol Solar Power ion (100 MW), allin Spain.

The first three units of Solnova in the foreground, with the two towers of the PS10 and PS20 solar power stations in the background.

A solar thermal collector system gathers the heat from the solar radiation and gives it to the heat transport fluid. The heat-transport fluid receives the heat from the collector and delivers it to the thermal storage tank, boiler steam generator, heat exchanger etc. Thermal

storage system stores heat for a few hours. The heat is released during cloudy hours and at

night. Thermal-electric conversion system receives thermal energy and drives steam

turbine generator or gas turbine generator. The electrical energy is supplied to the

electrical load or to the AC grid. Applications of solar thermal energy systems range from

simple solar cooker of 1 kW rating to complex solar central receiver thermal power plant

of 200 MW rating.

SOLAR COLLECTORS

Solar thermal energy is the most readily available source of energy. The Solar energy is most important kind of non-conventional source of energy which has been used since ancient times, but in a most primitive manner. The abundant solar energy available is suitable for harnessing for a number of applications. The application of solar thermal energy system ranges from solar cooker of 1 kw to power plant of 200MW. These systems are grouped into low temperature (<150oC), medium temperature (150-300oC) applications.

Solar Collectors

Solar collectors are used to collect the solar energy and convert the incident radiations into thermal energy by absorbing them. This heat is extracted by flowing fluid (air or water or mixture with antifreeze) in the tube of the collector for further utilization in different applications. The collectors are classified as;

- Non concentrating collectors

- Concentrating (focusing) collectors

Non Concentrating Collectors

In these collectors the area of collector to intercept the solar radiation is equal to the absorber plate and has concentration ratio of 1. Flat Plate Collectors (Glaze Type) Flat plate collector is most important part of any solar thermal energy system. It is simplest in design and both direct and diffuse radiations are absorbed by collector and converted into useful heat. These collectors are suitable for heating to temperature below 100oC. The main advantages of flat plate collectors are:

- It utilizes the both the beam as well as diffuse radiation for heating.

- Requires less maintenance.

Disadvantages

- Large heat losses by conduction and radiation because of large area.

- No tracking of sun.

- Low water temperature is achieved.

The constructional details of flat plate collector is given below

- Insulated Box: The rectangular box is made of thin G.I sheet and is insulated from sides and bottom using glass or mineral wool of thickness 5 to 8 cm to reduce losses from

conduction to back and side wall. The box is tilted at due south and a tilt angle depends on the latitude of location. The face area of the collector box is kept between 1 to 2 m2.

- Transparent Cover: This allows solar energy to pass through and reduces the convective heat losses from the absorber plate through air space. The transparent tampered glass cover is placed on top of rectangular box to trap the solar energy and sealed by rubber gaskets to prevent the leakage of hot air. It is made of plastic/glass but glass is most favourable because of its transmittance and low surface degradation. However with development of improved quality of plastics, the degradation quality has

been improved. The plasticsare available at low cost, light in weight and can be used to

make tubes, plates and cover but are suitable for low temperature application 70-120oC with single cover plate or up to 150oC using double cover plate. The thickness of glass cover 3 to 4 mm is commonly used and 1 to 2 covers with spacing 1.5 to 3 cm are generally used between plates. The temperature of glass cover is lower than the absorber plate and is a good absorber of thermal energy and reduces convective and radiative losses of sky.

- Absorber Plate: It intercepts and absorbs the solar energy. The absorber plate is made of copper, aluminum or steel and is in the thickness of1 to 2 mm. It is the most important part of collector along with the tubes products passing the liquid or air to be heated. The plate absorbs the maximum solar radiation incident on it through glazing (cover plate) and transfers the heat to the tubes in contact with minimum heat losses to atmosphere. The plate is black painted and provided with selective material coating to increase its absorption and reduce the emission. The absorber plate has high absorption (80-95%) and low transmission/reflection.

- Tubes: The plate is attached to a series of parallel tubes or one serpentine tube through which water or other liquid passes. The tubes are made of copper, aluminum or steel in the diameter 1 to 1.5 cm and are brazed, soldered on top/bottom of the absorber water equally in all the tubes and collect it back from the other end. The header pipe is made of same material as tube and of larger diameter. Now-a-days the tubes are made of plastic but they have low thermal conductivity and higher coefficient of expansion than metals.

Copper and aluminum are likely to get corroded with saline liquids and steel tubes within hibitors are used at such places.

Removal of Heat: These systems are best suited to applications that require low temperatures. Once the heat is absorbed on the absorber plate it must be removed fast and delivered to the place of storage for further use. As the liquid circulates through the tubes, it absorbs the heat from absorber plate of the collectors. The heated liquid moves slowly and the losses from collector will increase because of rise of high temperature of collector and will lower the efficiency. Flat-plate solar collectors are less efficient in cold weather than in warm weather. Factors affecting the Performance of Flat Plate Collector.

The different factors affecting the performance of system are:

- Incident Solar Radiation: The efficiency of collector is directly related with solar radiation falling onit and increases with rise in temperature.

- Number of Cover Plate: The increase in number of cover plate reduces the internal convective heat losses but also prevents the transmission of radiation inside the collector. More than two cover plate should not be used to optimize the system.

- Spacing: The more space between the absorber and cover plate the less internal heat losses. The collector efficiency will be increased. However on the other hand, increase in space between them provides the shading by side wall in the morning and evening and reduces the absorbed solar flux by 2-3% of system. The spacing between absorber and cover plate is kept 2-3 cm to balance the problem.

- Collector Tilt: The flat plate collectors do not track the sun and should be tilted at

angle of latitude of the location for an average better performance. However with changing declination angle with seasons the optimum tilt angle is kept Φ ± 15o.

The collector is placed with south facing at northern hemisphere to receive maximum radiation throughout the day.

- Selective Surface: Some materials like nickel black (α= 0.89, ε= 0.15) and black chrome (α= 0.87, ε= 0.088), copper oxide (α= 0.89, ε= 0.17) etc. are applied chemically on the surface of absorber in a thin layer of thickness 0.1 μm. These chemicals have high degree of absorption (α) to short wave radiation (< 4 μm) and low emission (ε) of long wave radiations (> 4 μm). The higher absorption of solar energy increase the temperature of absorber plate and working fluid. The top losses reduce and the efficiency of the

collector increases. The selective surface should be able to withstand high temperature of 300-400oC, cost less, should not oxidize and be corrosive resistant. The property of material should not change with time.

- Inlet Temperature: With increase in inlet temperature of working fluid the losses increase to ambient. The high temperature fluid absorbed the less heat from absorber plate because of low temperature difference and increases the top loss coefficient. Therefore the efficiency of collector get reduced with rise in inlet temperature.

- Dust on cover Plate: The efficiency of collector decreases with dust particles on the cover plate because the transmission radiation decreases by 1%. Frequent cleaning is required to get the maximum efficiency of collector.

Concentrating Collectors

Concentrating collector is a device to collect solar energy with high intensity of solar radiation on the energy absorbing surface. Such collectors use optical system in the form of reflectors or refractors.

These collectors are used for medium (100-300o C) and high-temperature (above 300oC) applications such as steam production for the generation of electricity. The high temperature is achieved at absorber because of reflecting arrangement provided for concentrating the radiation at required location using mirrors and lenses.

These collectors are best suited to places having more number of clear days in a year.

The area of the absorber is kept less than the aperture through which the radiation passes, to concentrate the solar flux. These collectors require tracking to follow the sun because of optical system. The tracking rate depends on the degree of concentration ratio and needs frequent adjustment for system having high concentration ratio. The efficiency of these collectors lies between 50-70%. The collectors need more maintenance than FPC because of its optical system. The concentrating collectors are classified on the basis of reflector used; concentration ratio and tracking method adopted.

FPC with Reflectors

The mirrors are placed as reflecting surface to concentrate more radiations on FPC absorber. The fluid temperature is higher by 30oC than achieved in FPC. These collections utilize direct and diffuse radiation.

Lens Focusing Type

The fresnel lenses are used to concentrate the radiation at its focus. The lower side of lenses is grooved so that radiation concentrates on a focus line.

Compound Parabolic Collectors

These collectors are line focusing type. The compound parabolic collectors have two parabolic surfaces to concentrate the solar radiation to the absorber placed at bottom.

These collectors have high concentration ratio and concentrator is moving to track the sun.

Cylindrical Parabolic Collectors

The troughs concentrate sunlight onto a receiver tube, placed along the focal line of the trough. The temperature at the absorber tube is obtained at nearly 400o C. The absorber in these collectors is moving to receive the reflected radiations by reflector, while the concentrators (trough) remains fixed. Because of its parabolic shape, it can focus the sun at 30 to 100 times its normal intensity (concentration ratio) on a receiver. The heat transfer medium carries the heat at one central place for further utilization.

Parabolic Dish Collector

The collectors have mirror-like reflectors and an absorber at the focal point. These collectors are point focusing type. The concentrating ratio of these collectors is 100 and temperature of the receiver can reach up to 2000o C. These collectors have higher efficiency for converting solar energy to electricity in the small-power plant. In some systems, a heat engine, such as a Stirling engine, is connected to the receiver to generate electricity.

Center Receiver Type (Solar Power Tower)

These collectors are used to collect the large solar energy at one point. This system uses 100-10000 of flat tracking mirror scaled heliostats to reflect the solar energy to central receiver mounted on tower. The energy can be concentrated as much as 1,500 times than that of the energy coming in, from the sun. The losses of energy from the system are minimized as solar energy is being directly transferred by reflection from the heliostats to a single receiver where the sun’s rays heat a fluid to produce steam.

Advantages of concentrating collector over flat collector

- The size of the absorber can be reduced that gives high concentration ratio.

- Thermal losses are less than FPC. However small losses occur in the concentrating collector because of its optical system as well as by reflection, absorption by mirrors and lenses.

- The efficiency increases at high temperatures.

- In these collectors the area intercepting the solar radiation is greater than the absorber area.

- These collectors are used for high-temperature applications.

- Reflectors can cost less per unit area than flat plate collectors.

- Focusing or concentrating systems can be used for electric power generation when not used for heating or cooling

- Little or no anti freeze is required to protect the absorber in a concentrator system whereas the entire solar energy collection surface requires anti freeze protection in a flat plate collector

Disadvantages

- Out of the beam and diffuse solar radiation components, only beam component is collected in case of focusing collectors because diffuse component cannot be reflected and is thus lost.

- In some stationary reflecting systems it is necessary to have a small absorber to track the sun image; in others the reflector may have to be adjustable more than one position if year round operation is desired; in other words costly orienting systems have to be used to track the sun.

- Additional requirements of maintenance particular to retain the quality of reflecting surface against dirt, weather, oxidation etc.

- Non –uniform flux on the absorber whereas flux in flat-plate collectors in uniform.

- Additional optical losses such as reflectance loss and the intercept loss, so they introduce additional factors in energy balances.

- High initial cost.

Solar Air Heaters

Air stream is heated by the back side of the collector plate in flat plate collector. Fins attached to the plate increase the contact surface. The back side of the collector is heavily insulated with mineral wool or some other material. If the size of collector is large, a blower is used to draw air into the collector and transmit the hot air to dryer.

The most favorable orientation of a collector for heating only is facing due south at an inclination angle to the horizontal equal to the latitude plus 150. The use of air as the heat transport fluid eliminates both freezing and corrosion problems and small air leaks are of less concern than water leaks

Disadvantages:

- Need of handling larger volumes of air than liquids due to low density of air as working substance.

- Thermal capacity of the air is low.

- They have relatively high fluid circulation costs (especially if the rock heat storage unit is not carefully designed)

- They have relatively large volumes of storage (roughly three times as much volume as for water heat-storage)

- They have a higher noise level.

- The system has difficulty of adding conventional absorption air-conditioners to air systems

- The space is required for ducting.

Types of Air Heaters

- Non porous absorber in which air stream does not flow through the absorber plate

- Porous absorber that includes slit and expanded material, transpired honey comb and over lapped glass plate

- Non-porous absorber plate type collectors: A non-porous absorber may be cooled by the air stream flowing over both sides of the plate. In most of the designs, the air flows behind the absorbing surface. Air flow above the upper surface increases the convection losses from the cover plate and therefore is not recommended if the air inlet temperature rise at the collector are large.

Transmission of the solar radiation through the transparent cover system and its absorption is identical to that of a liquid type flat-plate collector. To improve collection efficiency selective coating may beapplied provided there is no much cost.

Due to low heat transfer rates, efficiencies are lower than liquid solar heaters under the same radiation intensity and temperature conditions. Performance of air heaters is improved by:

- Roughening the rear of the plate to promote turbulence and improve the convective heat transfer coefficient

- Adding fins to increase heat transfer surface. Usually turbulence is also increased which enhances the convective heat transfer. Absorption of solar radiation is improved due to surface radioactive characteristics and the geometry of the corrugations, which help in trapping the reflected radiation.

- Collectors with porous absorbers: The main drawback of the non-porous absorber plate is the necessity of absorbing all incoming radiation over the projected area from a thin layer over the surface, which is in the order of a few microns.

Unless selective coatings are used, radiative losses from the absorber plate are excessive, therefore, the collection efficiency cannot be improved. Too many surfaces and too much restriction to air flow will require a larger fan and a larger amount of energy to push the air through. The energy required for this cancels out saving from using solar energy, particularly if fan is electrical and if the amount of energy which is burned at the power plant to produce the electrical energy is included.

The solar air heating utilizing a transpired honey comb is also favorable since the flow cross section is much higher. Crushed glass layers can be used to absorb solar radiation and heat the air. A porous bed with layers of broken bottles can be readily used for agricultural drying purposes with minimum expenditure. The overlapped glass plate air heater can be considered as a form of porous matrix, although overall flow direction is along the absorber plates instead of being across the matrix.

Applications of Solar air heaters

- Heating buildings.

- Drying agricultural produce and lumber.

- Heating green houses.

- Air conditioning building sutilizing desiccant beds or a absorption refrigeration process.

- Heat sources for a heat engine such as a Brayton or Stirling cycle.

Flat plate collectors (non-concentrating)

Where temperatures below about 90oC are adequate as they are for space and service water heating flat plate collectors, which are of the non-concentrating type, are particularly convenient. They are made in rectangular panels from about 1.7 to 2.9 sq.m, in area, and are relatively simple to construct and erect. Flat plates can collect and absorb both direct and diffuse solar radiation, they are consequently partially effective even on cloudy days when there is no direct radiation.

Flat plate solar collectors may be divided into two main classifications based on the type of heat transfer fluid used.

Fig. 2.4. Liquid heating flat plate collector

A. Liquid heating Flat Plate Collector

Liquid heating flat plate collectors are used for heating water and non-freezing aqueous solutions.

There are many flat-plate collector designs, but most are based on the principle shown in fig 2.4. It is the plate and tube type collector. It basically

consists of a flat surface with high absorptivity for solar radiation called the absorbing surface. Typically a metal plate, usually of copper, steel or aluminum material with tubing of copper in thermal contact with the plates are the most commonly used materials. The absorber plate is usually made from a metal sheet 1 to 2 mm in thickness, while the tubes, which are also of metal, range in diameter from 1 to 1.5cm. They are soldesed, brazed or clamped to the bottom of the absorber plate with the pitch ranging from 5 to 15 Cm, In some designs, the tubes are also in line and integral with the absorber plate.

The primary function of the absorber is to absorb maximum radiation reaching it through the glazing, to lose maximum heat upward to the atmosphere and down ward through the back of the container and to transfer the retained heat to the working fluid. Black painted absorbers are preferred because they are considerably cheaper and good absorbers of radiation.

Heat is transferred from the absorber plate to a point of use by circulation of fluid (usually water) across the solar heated surface. Thermal insulation of 5 to 10cm. Thickness is usually placed behind the absorber plate to prevent the heat losses from the rear surface. Insulation materials is generally mineral wool or glass wool or fiber glass.

The front covers are generally glass that is transparent to incoming solar radiation and opaque to the infra-red re-radiation from the absorber. The glass covers act as a convection shield to reduce the losses from the absorber plate beneath. The glass thickness of 3 and 4 mm are commonly used. The usual practice is to have 2 covers with specific ranging from 1.5 to 3cm.

Advantages of second glass which is added above the first one are

- Losses due to air convection are further reduced. This is important in windy areas.

- Radiation losses in the infra-red spectrum are reduced by a further 25%, because half of the 50% which is emitted out wards from the first glass plate is back radiated.

(ii) Concentrating (focusing) type solar collector

Focusing collector or concentrating type solar collector is a device to collect solar energy with high intensity of solar radiation on the energy absorbing surface. Such collectors generally use optical system in the form of reflectors or refractors. A focusing collector is a special form of flat-plate collector modified by introducing a reflecting or refracting surface between the Solar Radiation and the absorber. In these collectors radiation falling on a relatively large area is focused on to a receiver or absorber of considerably smaller area. As a result of the energy concentration, fluids can be heated to temperatures of 5000C or more.

Fig. 2.5 Parabolic concentrating collector

A Schematic diagram of a typical concentrating collector is shown in fig 2.5 the collector consists of a concentrator and a receiver. The concentrator shown is a mirror reflector having the shape of a cylindrical parabola. It focuses the sunlight on to its axis where it is absorbed on the surface of the absorber tube and transferred to the fluid flow through it. A concentric glass cover around the absorber tube helps in reducing the convective and radiative losses to the surroundings. In order that the sun’s rays should always be focussed on to the absorber tube, the concentrator has to be rotated. This movement is called tracking in the case of cylindrical parabolic concentrators, rotation about a single axis is generally required. Fluid temperatures up to around 300oC can be achieved in cylindrical parabolic focussing collector system.

The generation of still higher working temperatures is possible by using parabolic reflectors as shown in fig 2.6 which have a point focus.

17

Non-Conventional Energy Sources

A paraboloidal dish collector brings solar radiation to a focus at a point actually a small central volume. A dish 6.6m diameter has been made from about 200 curved mirror segments forming a paraboloidal surface. The absorber, located at the focus, is a cavity made of zirconium-copper alloy with a black chrome selective coating. The heat-transport fluid flows into and out of the absorber cavity through pipes bonded to the interior. The dish can be turned automatically about two axes so that the sun is always kept in a line with the focus and the base of the paraboloidal dish. Thus, the can be fully tracked at essentially all times.

Fig 2.6 Dish Collector (Point Focus)

2.6.3. Solar Cooker

In our country energy consumed for cooking shares a major portion of the total energy consumed in a year. In villages 95% of the consumption goes only to cooking. Verity of fuel like coal, kerosene, cooking gas, firewood, dung cakes and agricultural waste are used the energy crisis is affecting everyone. It is affecting the fuel bills for those who use it for heating the houses and cooking their food. The poor of the developing countries who have been using dry wood, picked up from the fields and forests as domestic fuel, have been affected in their own way, due to scarcity of domestic fuel in the rural areas. At present, fire wood and cow dung too precious to allowed to be used for burning and cooking. It is very useful to improve the fertility of the soil, it should be used in proper way. The supply of wood is also fast depleting because of the indiscriminate felling of trees in the rural areas and the denudation of forests. There is a rapid deterioration in the supply of these

fossil fuels like coal, kerosene or cooking gas. The solution for the above problem is the hardnesing of solar energy for cooking purpose.

The most important is that the solar cooker is a great fuel saver. The department of new conventional energy source has calculated that a family using a solar cooker 275 days a year would save 800kgs of fire wood or 65 liters of kerosene. Similarly an industrial Canteen or a Hostel mess using the larger community solar cooker which can cook for 20 to 25 people could save 400kgs of fire wood or 335 liters of kerosene per year.

Flat plate collector absorbs both beam and diffuse components of radiant energy. The

absorber plate is a specially treated blackened metal surface. Sun rays striking the

absorber plate are absorbed causing rise of temperature of transport fluid. Thermal

insulation behind the absorber plate and transparent cover sheets (glass or plastic) prevent

loss of heat to surroundings.

Applications of flat plate collector:

- Solar water heating systems for residence, hotels, industry.

- Desalination plant for obtaining drinking water from sea water.

- Solar cookers for domestic cooking.

- Drying applications.

- Residence heating. Losses in flat plate collector:

- Shadow effect: Shadows of some of the neighbor panel fall on the surface ofthe collector where

the angle of elevation of the sun is less than 15o(sun-rise and sunset).

Shadow factor = surfaceof thecollector recievinglight

Total surfaceof thecollector

Shadow factor is less than 0.1 during morning and evening. The effective hours of solar collectors

are between 9AM and 5PM.

- Cosine loss factor: For maximum power collection, the surface of collector should receive the

sun rays perpendicularly. If the angle between the perpendicular to the collector surface and the direction of sun rays is θ, then the area of solar beam intercepted by the collector surface is proportional to cosθ.

- Reflective loss factor: The collector glass surface and the reflector surface collect dust, dirt, moisture etc. The reflector surface gets rusted, deformed and loses the shine. Hence, the efficiency of the collector is reduced significantly with passage of time.

Maintenance of flat plate collector:

- Daily cleaning

- Seasonal maintenance (cleaning, touch-up paint)

- Yearly overhaul (change of seals, cleaning after dismantling)

Parabolic trough collector:

Parabolic trough with line f ocusing reflecting surface provides concentratio n ratios from

30 to 50. Hence, temperature as high as 300oC can be attained. Light is focused on a

central line of the parabolic trough. The pipe located along the centre line absorbs the heat

and the working fluid is circu lated trough the pipe.

Paraboloid dish collectors:

The beam radiation is reflected by paraboloid dish surface. The point foc us is obtained with CR (above 1000) and temperatures around 1000oC.

Based on the temperature:

- Low temperature collector

- Medium temperature collector

- High temperature collector

Low temperature collecto r:

Low-temperature collectors[ edit]

Main article: Solar thermal collector

Glazed solar collectors are d esigned primarily for space heating. They re-cir culate building air through a solar air panel where the air is heated and then directed back into the building. These solar space heating systems require at least two penetrations into the building and only perform when the air in the solar collector is warmer than the building room temperature. Most glazed collectors are used in the residential sector.

Unglazed, "transpired" air collector

Unglazed solar collectors are primarily used to pre-heat make-up ventilation air in commercial, industrial and institutional buildings with a high ventilation load. They turn building walls or sections of walls into low cost, high performance, unglazed solar collectors. Heat conducts from the absorber surface to the thermal boundary layer of air

1 mm thick on the outside of the absorber and to air that passes behind the absorber. The boundary layer of air is drawn into a nearby perforation before the heat can escape by convection to the outside air. The heated air is then drawn from behind the absorber plate into the building's ventilation system.

A Trombe wall is a passive solar heating and ventilation system consisting of an air channel sandwiched between a window and a sun-facing thermal mass. During the ventilation cycle, sunlight stores heat in the thermal mass and warms the air channel causing circulation through vents at the top and bottom of the wall. During the heating cycle the Trombe wall radiates stored heat.

Solar roof ponds are unique solar heating and cooling systems developed by Harold Hay in the 1960s. A basic system consists of a roof-mounted water bladder with a movable insulating cover. This system can control heat exchange between interior and exterior environments by covering and uncovering the bladder between night and day. When heating is a concern the bladder is uncovered during the day allowing sunlight to warm the water bladder and store heat for evening use. When cooling is a concern the covered bladder draws heat from the building's interior during the day and is uncovered at night to radiate heat to the cooler atmosphere.

Solar space heating with solar air heat collectors is more popular in the USA and Canada than heating with solar liquid collectors since most buildings already have a ventilation system for heating and cooling. The two main types of solar air panels are glazed and unglazed.

Medium temperature collector:

Solar drying

Solar thermal energy can be useful for drying wood for construction and wood fuels such as wood chips for combustion. Solar is also used for food products such as fruits, grains, and fish. Crop drying by solar means is environmentally friendly as well as cost effective while improving the quality. The less money it takes to make a product, the less it can be sold for, pleasing both the buyers and the sellers. Technologies in solar drying include ultra low cost pumped transpired plate air collectors based on black fabrics. Solar thermal energy is helpful in the process of drying products such as wood chips and other forms of biomass by raising the temperature while allowing air to pass through and get rid of the moisture.

Cooking

Solar cookers use sunlight for cooking, drying and pasteurization. Solar cooking offsets fuel costs, reduces demand for fuel or firewood, and improves air quality by reducing or removing a source of smoke. The simplest type of solar cooker is the box cooker first

built by Horace de Saussure in 1767. A basic box cooker consists of an insulated container with a transparent lid. These cookers can be used effectively with partially overcast skies and will typically reach temperatures of 50–100 °C. Concentrating solar cookers use reflectors to concentrate solar energy onto a cooking container. The most common reflector geometries are flat plate, disc and parabolic trough type. These designs cook faster and at higher temperatures (up to 350 °C) but require direct light to function properly. The Solar Kitchen in Auroville, India uses a unique concentrating technology known as the solar bowl. Contrary to conventional tracking reflector/fixed receiver systems, the solar bowl uses a fixed spherical reflector with a receiver which tracks the focus of light as the Sun moves across the sky. The solar bowl's receiver reaches temperature of 150 °C that is used to produce steam that helps cook 2,000 daily meals.

High temperature collector

Where temperatures below about 95 °C are sufficient, as for space heating, flat-plate collectors of the non-concentrating type are generally used. Because of the relatively high heat losses through the glazing, flat plate collectors will not reach temperatures much above 200 °C even when the heat transfer fluid is stagnant. Such temperatures are too low for efficient conversion to electricity.

The efficiency of heat engines increases with the temperature of the heat source. To achieve this in solar thermal energy plants, solar radiation is concentrated by mirrors or lenses to obtain higher temperatures – a technique called Concentrated Solar Power (CSP). The practical effect of HIGH EFFICIENCIES is to reduce the plant's collector size and total land use per unit power generated, reducing the environmental impacts of a power plant as well as its expense.

As the temperature increases, different forms of conversion become practical. Up to 600 °C, steam turbines, standard technology, have an efficiency up to 41%. Above 600 °C, gas turbines can be more efficient. Higher temperatures are problematic because different materials and techniques are needed. One proposal for very high temperatures is to use liquid fluoride salts operating between 700 °C to 800 °C, using multi-stage turbine systems to achieve 50% or more thermal efficiencies.[25] The higher operating temperatures permit the plant to use higher-temperature dry heat exchangers for its thermal exhaust, reducing the plant's water use – critical in the deserts where large solar plants are practical. High temperatures also make heat storage more efficient, because more watt-hours are stored per unit of fluid.

Commercial concentrating solar thermal power (CSP) plants were first developed in the 1980s. The world’s largest solar thermal power plants are now the 370 MW Ivanpah Solar Power Facility, commissioned in 2014, and the 354 MW SEGS CSP installation both located in the Mojave Desert of California, where several other solar projects have been realized as well. With the exception of the Shams solar power station, built in 2013 near Abu Dhabi, the United Arab Emirates, all other 100 MW or larger CSP plants are either located in the United States or in Spain.

The principal advantage of CSP is the ability to efficiently add thermal storage, allowing the dispatching of electricity over up to a 24-hour period. Since peak electricity demand typically occurs at about 5 pm, many CSP power plants use 3 to 5 hours of thermal

storage.[26] With current tech nology, storage of heat is much cheaper and more efficient than storage of electricity. In this way, the CSP plant can produce electricity day and night. If the CSP site has predictable solar radiation, then the CSP plant becomes a reliable power plant. Reliability can further be improved by installi ng a back-up combustion system. The back-up system can use most of the CSP plant, wh ich decreases the cost of the back-up syste m.

CSP facilities utilize high electrical conductivity materials, such as co pper, in field power cables, grounding net works, and motors for tracking and pumping fluids, as well as in the main generator and hig h voltage transformers.

With reliability, unused desert, no pollution, and no fuel costs, the obstacles for large deployment for CSP are co st, aesthetics, land use and similar factors for the necessary connecting high tension liness. Although only a small percentage of the dese rt is necessary to meet global electricity de mand, still a large area must be covered with mirrors or lenses to obtain a significant amou nt of energy. An important way to decrease cost is the use of a SIMPLE design.

When considering land us e impacts associated with the exploration and extraction through to transportation and conversion of fossil fuels, which are used for most of our electrical power, utility-scale solar power compares as one of the most land-efficient energy resources available.

System designs

During the day the sun has different positions. For low concentration systems (and low temperatures) tracking can be avoided (or limited to a few positions per year) if non-imaging optics are used. For higher concentrations, however, if the mirror s or lenses do not move, then the focus of the mirrors or lenses changes (but also in these cases non-imaging optics provides th e widest acceptance angles for a given concentration). Therefore it seems unavoidable that there needs to be a tracking system that follows the position of the sun (for solar photovoltaic a solar tracker is only optional). The tracking system increases the cost a nd complexity. With this in mind, different designs can be distinguished in how they concentrate the light and track the position of the s un.

Parabolic trough designs

Parabolic trough power plants use a curved, m irrored trough which reflects the direct solar radiation onto a glass tube containing a fluid (also called a receiver, absorber or collector) running the length of the trough, po sitioned at the focal point of the reflectors. The trough is p arabolic along one axis and linear in the orthogonal axis. For change of the daily position of the sun perpendicular to the receiver, the trough tilts east to west so that the direct rad iation remains

focused on the receiver. How ever, seasonal changes in the in angle of sunlight parallel to the trough does not require adju stment of the mirrors, since the light is simply concentrated elsewhere on the receiver. Th us the trough design does not require tracking on a second axis. The receiver may be enclosed in a glass vacuum chamber. The vacuum significantly reduces convective heat loss.

A fluid (also called heat transfer fluid) passes through the receiver and becomes very hot. Common fluids are synthetic oil, molten salt and pressurized steam. The fluid containing the heat is transported to a heat engine where about a third of the heat is converted to electricity.

Full-scale parabolic trough systems consist of many such troughs laid out in parallel over a large area of land. Since 1985 a solar thermal system using this principle has been in full operation in California in the United States. It is called the Solar Energy Generating Systems(SEGS) system.[29] Other CSP designs lack this kind of long experience and therefore it can currently be said that the parabolic trough design is the most thoroughly proven CSP technology.

Power tower designs

Power towers (also known as 'central tower' power plants or 'heliostat' power plants) capture and focus the sun's thermal energy with thousands of tracking mirrors (called heliostats) in roughly a two square mile field. A tower resides in the centre of the heliostat field. The heliostats focus concentrated sunlight on a receiver which sits on top of the tower. Within the receiver the concentrated sunlight heats molten salt to over 1,000°F (538°C). The heated molten salt then flows into a thermal storage tank where it is stored, maintaining 98% thermal efficiency, and eventually pumped to a steam generator. The steam drives a standard turbine to generate electricity. This process, also known as the "Rankine cycle" is similar to a standard coal-fired power plant, except it is fueled by clean and free solar energy.

The advantage of this design above the parabolic trough design is the higher temperature. Thermal energy at higher temperatures can be converted to electricity more efficiently and can be more cheaply stored for later use. Furthermore, there is less need to flatten the ground area. In principle a power tower can be built on the side of a hill. Mirrors can be flat and plumbing is concentrated in the tower. The disadvantage is that each mirror must have its own dual-axis control, while in the parabolic trough design single axis tracking can be shared for a large array of mirrors.

Dish designs

A parabolic solar dish concentrating the sun's

rays on the heating element of a Stirling engine.	Fresnel reflector

CSP-Stirling is known to have the highest efficiency of all solar technologies around 30% compared to solar PV approximately 15%, and is predicted to be able to produce the cheapest energy among all renewable energy sources in high scale production and hot areas, semi deserts etc. A dish Stirling system uses a large, reflective, parabolic dish (similar in shape to satellite television dish). It focuses all the sunlight that strikes the dish up onto a single point above the dish, where a receiver captures the heat and transforms it into a useful form. Typically the dish is coupled with a Stirling engine in a Dish-Stirling System, but also sometimes a steam engine is used. These create rotational kinetic energy that can be converted to electricity using an electric generator.

Fresnel technologies

A linear Fresnel reflector power plant uses a series of long, narrow, shallow-curvature (or even flat) mirrors to focus light onto one or more linear receivers positioned above the mirrors. On top of the receiver a small parabolic mirror can be attached for further focusing the light. These systems aim to offer lower overall costs by sharing a receiver between several mirrors (as compared with trough and dish concepts), while still using the simple line-focus geometry with one axis for tracking. This is similar to the trough design (and different from central towers and dishes with dual-axis). The receiver is stationary and so fluid couplings are not required (as in troughs and dishes). The mirrors also do not need to support the receiver, so they are structurally simpler. When suitable aiming strategies are used (mirrors aimed at different receivers at different times of day), this can allow a denser packing of mirrors on available land area.

Rival single axis tracking technologies include the relatively new linear Fresnel reflector (LFR) and compact-LFR (CLFR) technologies. The LFR differs from that of the parabolic trough in that the absorber is fixed in space above the mirror field. Also, the reflector is composed of many low row segments, which focus collectively on an elevated long tower receiver running parallel to the reflector rotational axis.

Prototypes of Fresnel lens concentrators have been produced for the collection of thermal energy by International Automated Systems. No full-scale thermal systems using Fresnel lenses are known to be in operation, although products incorporating Fresnel lenses in conjunction with photovoltaic cells are already available.[41]

Micro-CSP

Micro-CSP is used for community-sized power plants (1 MW to 50 MW), for industrial, agricultural and manufacturing 'process heat' applications, and when large amounts of hot water are needed, such as resort swimming pools, water parks, large laundry facilities, sterilization, distillation and other such uses.

Enclosed parabolic trough

The enclosed parabolic trough solar thermal system encapsulates the components within an off-the-shelf greenhouse type of glasshouse. The glasshouse protects the components from the elements that can negatively impact system reliability and efficiency. This protection importantly includes nightly glass-roof washing with optimized water-efficient off-the-shelf automated washing systems.[42] Lightweight curved solar-reflecting mirrors

are suspended from the ceiling of the glasshouse by wires. A single-axis tracking system positions the mirrors to retrieve the optimal amount of sunlight. The mirrors concentrate the sunlight and focus it on a network of stationary steel pipes, also suspended from the glasshouse structure.[43] Water is pumped through the pipes and boiled to generate steam when intense sun radiation is applied. The steam is available for process heat. Sheltering the mirrors from the wind allows them to achieve higher temperature rates and prevents dust from building up on the mirrors as a result from exposure to humidity.[42]

Heat collection and exchange:

More energy is contained in higher frequency light based upon the formula of E  hυ , where h is the Planck constant and v is frequency. Metal collectors down convert higher frequency light by producing a series of Compton shifts into an abundance of lower frequency light. Glass or ceramic coatings with high transmission in the visible and UV and effective absorption in the IR (heat blocking) trap metal absorbed low frequency light from radiation loss. Convection insulation prevents mechanical losses transferred through gas. Once collected as heat, thermos containment efficiency improves significantly with increased size. Unlike Photovoltaic technologies that often degrade under concentrated light, Solar Thermal depends upon light concentration that requires a clear sky to reach suitable temperatures.

Heat in a solar thermal system is guided by five basic principles: heat gain; heat transfer; heat storage; heat transport; and heat insulation. Here, heat is the measure of the amount of thermal energy an object contains and is determined by the temperature, mass and specific heat of the object. Solar thermal power plants use heat exchangers that are designed for constant working conditions, to provide heat exchange. Copper heat exchangers are important in solar thermal heating and cooling systems because of copper’s high thermal conductivity, resistance to atmospheric and water corrosion, sealing and joining by soldering, and mechanical strength. Copper is used both in receivers and in primary circuits (pipes and heat exchangers for water tanks) of solar thermal water systems.

Heat gain is the heat accumulated from the sun in the system. Solar thermal heat is trapped using the greenhouse effect; the greenhouse effect in this case is the ability of a reflective surface to transmit short wave radiation and reflect long wave radiation. Heat and infrared radiation (IR) are produced when short wave radiation light hits the absorber plate, which is then trapped inside the collector. Fluid, usually water, in the absorber tubes collect the trapped heat and transfer it to a heat storage vault.

Heat is transferred either by conduction or convection. When water is heated, kinetic energy is transferred by conduction to water molecules throughout the medium. These molecules spread their thermal energy by conduction and occupy more space than the cold slow moving molecules above them. The distribution of energy from the rising hot water to the sinking cold water contributes to the convection process. Heat is transferred from the absorber plates of the collector in the fluid by conduction. The collector fluid is circulated through the carrier pipes to the heat transfer vault. Inside the vault, heat is transferred throughout the medium through convection.

Heat storage enables solar thermal plants to produce electricity during hours without sunlight. Heat is transferred to a thermal storage medium in an insulated reservoir during hours with sunlight, and is withdrawn for power generation during hours lacking sunlight. Thermal storage mediums will be discussed in a heat storage section. Rate of heat transfer is related to the conductive and convection medium as well as the temperature differences. Bodies with large temperature differences transfer heat faster than bodies with lower temperature differences.

Heat transport refers to the activity in which heat from a solar collector is transported to the heat storage vault. Heat insulation is vital in both heat transport tubing as well as the storage vault. It prevents heat loss, which in turn relates to energy loss, or decrease in the efficiency of the system.

As solar power has low density (kW/m2), therefore large area on the ground is covered by collectors. Flat plate collectors are used for low temperature applications. For achieving higher temperature of transport fluid, the sun rays must be concentrated and focused.

Concentration Ratio (CR):solar radiation surfaces(kW/m2 )

solar radiation at focus on surfaces of collector(kW/m2 )

CR = For flat plate collectors, CR = 1. Using heliostats with sun-tracking in two planes,

we obtain CR of the order of 1000. CR up to 100 can be achieved by using parabolic

trough collectors with sun tracking in one plane.

The performance of a collector is evaluated in terms of its collector efficiency which is

given as constant solar radiation (kW/m2), the collector efficiency decreases with the

increasing difference between the collector temperature and the outside temperature.